## Thong so 220kV
Parameter | Value | Unit
Line length | 117.794 | km
Nominal voltage | 220 | kV
Conductor type | ACSR
Conductor diameter (D) | 27.5 | mm
Conductor sections | 394/51.1 | mm2
The total heat capacity of the conductor (mCp) | 1310 | J ⁄ (m × °C)
Emissivity (ɛ) | 0.7
Static line rating | 850 | A
Elevation | 30–35 | m
Latitude | 11.758° N
Longitude | 109.020° E
The line runs in an east to west direction so azimuth of line (Zl) | 90°
Solar absorptivity (α) | 0.8
Conductor's surface area (A) | 0.0864 | m^2/meter
AC resistance at 20°C | 7.4766e-05 | Ω/m
AC resistance at 25°C | 7.6273e-05 | Ω/m
AC resistance at 75°C | 9.1338e-05 | Ω/m
AC resistance at 200°C | 0.000129 | Ω/m